## Slide 1
B17 Meter System Structure
Dekie Cheng
June 2023

## Slide 2
Physical Device Structure
This service will run on backend by specified interval time, and read the values from the physical device and store into DB tables
水表
立方米
电表KWh
总有功功率
正向有功总电能
合相功率因数
空调冷冻水流量计 累积流量(m3）
瞬时流量(m3/h)
瞬时流速(m/s)
进水温度
出水温度
瞬时热量（GJ/h）
累积热量(GJ)
压缩空气流量计
累积流量（Nm3）
瞬时流量(Nm3/h)
瞬时流速(m/s)
Watermeter1
Watermeter2
Watermeter3
….
Watermeter15
electricity meter1
electricity meter2
electricity meter3
….
electricity meter15
Air-conditioning chilled water flow meter1
Air-conditioning chilled water flow meter2
….
Air-conditioning chilled water flow meter15
RS485
RS485
RS485
RS485
172.1.1.1
172.1.1.2
172.1.1.3
172.1.1.n
Compressed air flowmeter1
Compressed air flowmeter2
….
Compressed air flowmeter15
Windows Service

## Slide 3
System Structure
This service will run on backend by specified interval time, and read the values from the physical device and store into DB tables
Display in Dashboard
SQL Server DB
Watermeter1
Watermeter2
Watermeter3
….
Watermeter15
electricity meter1
electricity meter2
electricity meter3
….
electricity meter15
Air-conditioning chilled water flow meter1
Air-conditioning chilled water flow meter2
….
Air-conditioning chilled water flow meter15
RS485
RS485
RS485
RS485
172.1.1.1
172.1.1.2
172.1.1.3
172.1.1.n
Compressed air flowmeter1
Compressed air flowmeter2
….
Compressed air flowmeter15
水表
立方米
空调冷冻水流量计 累积流量（Nm3）
瞬时流量(Nm3/h)
瞬时流速(m/s)
进水温度
出水温度
瞬时热量（GJ/h）
累积热量(GJ)
压缩空气流量计
累积流量（Nm3）
瞬时流量(Nm3/h)
瞬时流速(m/s)
Windows Service
电表KWh
总有功功率
正向有功总电能
合相功率因数

## Slide 4
SQL Server DB
Table Designation
No. | Category | Table Name | Description
1 | Basic Data | udtLNMeterCategory | will store the device category data, at present will include below 4 type: Water Meter(水表) Electricity Meter(电表) Air-conditioning chilled water flow meter(空调冷冻水流量计) Compressed air flow meter(压缩空气流量计)
 |  | udtLNSerialPortServer | will store all above category meter serial port server's HostIP, port and mbid no.
2 | Electricity Meter data | udtLNElectricityMeter | Store the electricity meter device information
 |  | udtLNElectricityMeterMaster | store data by day
 |  | udtLNElectricityMeterDetail | store data by hour
3 | Water Meter data | udtLNWaterMeter | store the water meter device relative information
 |  | udtLNWaterMeterMaster | store data by day
 |  | udtLNWaterMeterDetail | store data by hour
4 | Air-conditioning chilled water flow meter data | udtLNAirConditionWFlowMeterMaster | store data daily
 |  | udtLNAirConditionWFlowMeterMasterDetail | store data hourly
5 | Compressed air flow meter data | udtLNCompressedAirFlowMeterMaster | store data daily
 |  | udtLNCompressedAirFlowMeterDetail | store data hourly
6 | Log Data | udtLNRuntimeLogInfo | store the log information

## Slide 5
SQL Server DB
Table Designation for Basic Data

## Slide 6
SQL Server DB
Table Designation for Business Data

## Slide 7
Communication Seq for Water meter
Serial Port Server
IP: 10.200.7.183
Port: 5300
1. Connect to remote host
IP: 10.200.7.183
Port: 5300
2. Send read request by the command format
This Photo by Unknown Author is licensed under CC BY-SA
Accept the connection request
2. Read data from meter
TCP/IP
Water meter
RS485
RS485
RS485
RS485
3. Send data to client
3. Received data from host by the format
Windows Service
???
???

## Slide 8
Communication Seq for Electricity meter
Serial Port Server
IP: 10.200.7.183
Port: 5300
1. Connect to remote host
IP: 10.200.7.183
Port: 5300
2. Send read request by the command format
This Photo by Unknown Author is licensed under CC BY-SA
Accept the connection request
2. Read data from meter
TCP/IP
Electricity meter
RS485
RS485
RS485
RS485
3. Send data to client
3. Received data from host by the format
Windows Service

## Slide 9
Communication Seq for 空调冷冻水流量计
Serial Port Server
IP: 10.200.7.183
Port: 5300
1. Connect to remote host
IP: 10.200.7.183
Port: 5300
2. Send read request by the command format
This Photo by Unknown Author is licensed under CC BY-SA
Accept the connection request
2. Read data from meter
TCP/IP
Air-conditioning chilled
water flow meter
RS485
RS485
RS485
RS485
3. Send data to client
3. Received data from host by the format
Windows Service
例如在RTU方式下读取1号设备的流速，即读寄存器5，6共2个寄存器，命令如下:
01 03 00 04 00 02 85 CA （十六进制数字）
设备号 功能 起始寄存器 寄存器数目 效验和
其中85 CA 是16进制数值，是按照CRC-16 (BISYNCH，多项式是x16 + x15 + x2 + 1屏蔽字为0A001H)循环冗余算法得到的。请参考MODBUS有关资料了解进一步的算法。

## Slide 10
Communication Seq for 压缩空气流量计
Serial Port Server
IP: 10.200.2.87
Port: 5300
1. Connect to remote host
IP: 10.200.2.87
Port: 5300
2. Send read request by the command format
Accept the connection request
2. Read data from meter
TCP/IP
Compressed air flowmeter
RS485
RS485
RS485
3. Send data to client
3. Received data from host by the format
Windows Service
主站请求：01 03 00 00 00 0E C4 0E （指令为16进制）
命令格式：01为设备通讯地址，03为功能码，00 00 为起始寄存器地址，00 0E为寄存器长度，C4 0E为CRC校验码。
从站响应帧：01 03 1C D9 82 43 83 3C 3C 41 54 73 BF 45 B4 71 C7 42 48 00 00 00 00 AA 36 3F 7C 00 00 00 00 A0 BC
01为设备通讯地址 ，03为功能码，1C为字节数（一共读取了0E个也就是14个寄存器，每个寄存器两个字节共28个字节）
D9 82 43 83 为回来的第一个和第二个寄存器，代表了温度需要将字节调换重新排列再解析（顺序为3412）
也就是43 83 D9 82，解析数来和软件读取出来的一致都是263.699℃。

## Slide 11
Dashboard Structure
This Photo by Unknown Author is licensed under CC BY-SA
SQL Server DB
Sample